PD302 Installation Instructions

- Product Confirmation

| PD302 board | M3 screw |
| --- | --- |

- Component Name

| No. | Name | Instructions |
| --- | --- | --- |
| a | Mounting hole | Use M3 screw to install the PD302 board to the inverter |
| b | Connector | DB9 communication connector |
| c | Connector | Connect to the inverter |
| d | Station number switch | Switch station number(1~125) |
| e | Plastic handle | Remove PD302 board |
| f | Terminal resister | Terminal resister switch, the default state is OFF |

- Electrical Specifications

| Terminal form | Terminal name | Function name | Description |
| --- | --- | --- | --- |
| DB9 | 1 | --- | --- |
|  | 2 | --- | --- |
|  | 3 | Rxd/Txd-P | Receive/transmit data-P |
|  | 4 | CNTR-P 2) | Control-P |
|  | 5 | DGND | Data ground |
|  | 6 | VP 1) | Positive voltage |
|  | 7 | --- | --- |
|  | 8 | Rxd/Txd-N | Receive/transmit data-N |
|  | 9 | --- | --- |
| 1) The signal is only needed in bus cable endpoint station. |
| 2) The signal is alternative. |

- Profibus Switch Setting

The default setting of switch SW1 is OFF. When multiple machines are in communication, the switch of PD302 farthest from the position machine should be set as 220Ω. And other SW1 of PD302 stays the factory default state (OFF).

- Installation (SA3)

Step 1：Insert PD302 expansion card to SLOT 1 .DO NOT plug it in SLOT 2 or SLOT 3.

Step 2：Tighten the M3 screws with 4-6kgf.cm torque on the card as figure 2 shown.

Note：

1. For SA3–A frame inverters, remove the plastic part shown in figure 3, the result is shown in figure4.

2. When disassembling PD302, loosen the M3 screws first,then lift the plastic handle.

Figure 1                                             Figure 2

Figure 3                                 Figure 4

- Installation（SE3）

Step 1：Turn off the power.

Step 2：Open the top Cover of the inverter.

Step 3：Use the front rear as support and slide (a) in by pressing down as figure 1 shown.。

Figure 1

Note: (a)-Optional Card Housing; (b)-Hook, (c)-Slot

Step 4: Line up the connector (c) and (d), and press down the PD302 expansion card to the right position.

Figure 2

（a）(e)-Supporter, (b)-Plastic Handle, (c)-Male connector, (d)-Female connector

Step 5: Tighten two M3 screws with 4-6kgf.cm torque on the card. Install the Cover after wiring.

Figure 3

- Others

(To improve our products, the parameters and contents may be modified, please contact the agent or refer to Shihlin websites

(http://automation.seec.com.tw/) to download the latest version.